## Slide 1: Analysis of Power Production
Phuong Nguyen and Hugo Villegas

## Slide 2: Time-Series Power Measurements
power from exp. unit 11 (strawberry)
power from exp. unit 15 (grass or control)
power from exp. unit 11 minus 15
Each string rating within an experimental unit is 9.0-kW ca.

## Slide 3: Explain about saturated problem
Shared MPPT pair | Saturated | Severe
eu_8 + eu_16 | 386.6 h | 7.1 h
eu_10 + eu_18 | 539.8 h | 13.0 h
eu_13 + eu_21 | 342.8 h | 7.2 h
Total | 1,269.2 h | 27.3 h
What saturation is
The pair sum stops rising while irradiance keeps rising: the two units share one MPPT channel, the tracker runs out of headroom, and the shortfall is lost energy.
Detection (vat-v1)
  expected = theta(t) * ref
  deficit = 1 - measured / expected
  moderate: > 15 % for 15 min
  severe: > 30 % for 30 min
theta(t) is a slope in watts, so it can be checked against the 9.0 kW nameplate - and it reproduces it to within 4.1 %.
Four independent validations: (a) normalisation-free peer comparison on real data, (b) the inverter topology natural experiment, (c) the 9.0 kW nameplate cross-check, (d) injected ground truth.

## Slide 4
Results: 1,269.2 sampled hours of saturation across three shared MPPT channels, 27.3 h of it severe
Shared MPPT pair | moderate | severe | flagged days | apparent lost energy
eu_8 + eu_16 | 386.6 h | 7.1 h | 115 | 1,873 kWh
eu_10 + eu_18 | 539.8 h | 13.0 h | 147 | 2,538 kWh
eu_13 + eu_21 | 342.8 h | 7.2 h | 104 | 1,709 kWh
Total | 1,269.2 h | 27.3 h | - | 6,120 kWh
Energy is integrated over the detector gate domain (ref >= 0.70 and s > 0.6*expected). The same estimator applied to three pairs on independent trackers attributes only 409 kWh to them - 7 % of the claimed loss - and across all 117 cross-inverter independent pairs the median phantom loss is 92 kWh/pair. That is the residual precision of the energy figure.
The seasonal structure is coherent: flags peak in May-July, vanish in the acquisition gaps and when the pairs are off, and show a secondary peak on cold, clear February days.
Canonical artefact: saturation_flags.csv (51,005 x 21), regenerated from vat-v1 and locked by sat_work/canonical/CANONICAL_vat-v1.json. Guarded by 51 regression tests.
Known limitation: the raw deficit column is only defined inside the decision domain (ref >= 0.70, both units active, no data-quality flag); it is NaN elsewhere by design.